## Fuel 1
COMBUSTION ANALYSIS
Site Location |  |  |  |  | Std. Amb. Temperature |  |  | 517.0316 | Deg R
Fuel Designation |  | 1 | 1E,2W | East | Std. Amb. Pressure |  |  | 14.4498 | Psia
Site Elevation |  |  | 468 | Ft | Std. Amb. Pressure |  |  | 29.4188 | Bar
Ambient Temperature |  |  | 60 | Deg F | Atmospheric Density |  |  | 0.075005 | Lbm/Cuft
Ult Fract | Formula | Air/Fuel | Air | CO2 prod | H2O prod | N2 prod | SO2 prod |  | Htg Value
0.7076 | C | 11.51 | 8.1445 | 2.5926 | 0 | 6.2594 | 0 |  | 9972.2068
0.045236 | H2 | 34.29 | 1.5512 | 0 | 0.40428 | 1.1921 |  |  | 2763.7156
0.072673 | O2 | -4.3159 | -0.31365 | 0 | 0 | -0.24098 |  |  | 0
0.013655 | N2 | 0 | 0 | 0 | 0 | 0.013655 |  |  | 0
0.0067091 | S | 4.32 | 0.028983 | 0 | 0 | 0.022274 | 0.013405 |  | 26.7022
0.095964 | ASH | 0 | 0 | 0 | 0 | 0 |  |  | 0
0.058145 | H2O | 0 | 0 | 0 | 0.058145 | 0 | 0 |  | 0
Lbs Fuel |  | Air/Fuel | Stoich O2 | CO2 Prod | H2O Prod | N2 Prod | SO2 Prod | Total | HHV
0.99998 |  | 9.411 | 2.1805 | 2.5926 | 0.46242 | 7.2465 | 0.013405 | 10.315 | 12762.6246
Flue Gas | Exc O2% | Act O2 | O2 | CO2 | H2O | N2 | SO2 | Total | LHV
Analysis | 3 | 2.2459 | 0.065416 | 2.5926 | 0.46242 | 7.4634 | 0.013405 | 10.5973 | 12272.5951
|  | No. Moles | 0.0020443 | 0.058911 | 0.025668 | 0.26642 | 0.00020924 | 0.35325
|  | Mol Fract | 0.0057871 | 0.16677 | 0.072662 | 0.75419 | 0.00059231 | 29.9991 | Mol Wt.
Fuel Flow | Prod Flow | Fly ash % | With ash | Ash Load | Gas Temp | Heat Rel | ACFM |  | Comp
650000 | 6888243.3922 | 80 | 6938144.4831 | 1.6261 | 800 | 8295706001.9649 | 3580244.3527 |  | 1

## Fuel 2
COMBUSTION ANALYSIS
Site Location |  |  |  |  | Std. Amb. Temperature |  |  | 517.0316 | Deg R
Fuel Designation |  | 2 | 1E,2W | West | Std. Amb. Pressure |  |  | 14.4498 | Psia
Site Elevation |  |  | 468 | Ft | Std. Amb. Pressure |  |  | 29.4188 | Bar
Ambient Temperature |  |  | 60 | Deg F | Atmospheric Density |  |  | 0.075005 | Lbm/Cuft
Ult Fract | Formula | Air/Fuel | Air | CO2 prod | H2O prod | N2 prod | SO2 prod |  | Htg Value
0.5646 | C | 11.51 | 6.4985 | 2.0687 | 0 | 4.9945 | 0 |  | 7956.9078
0.0384 | H2 | 34.29 | 1.3167 | 0 | 0.34318 | 1.012 |  |  | 2346.048
0.1064 | O2 | -4.3159 | -0.45921 | 0 | 0 | -0.35281 |  |  | 0
0.009 | N2 | 0 | 0 | 0 | 0 | 0.009 |  |  | 0
0.00363 | S | 4.32 | 0.015682 | 0 | 0 | 0.012052 | 0.0072527 |  | 14.4474
0.0593 | ASH | 0 | 0 | 0 | 0 | 0 |  |  | 0
0.2188 | H2O | 0 | 0 | 0 | 0.2188 | 0 | 0 |  | 0
Lbs Fuel |  | Air/Fuel | Stoich O2 | CO2 Prod | H2O Prod | N2 Prod | SO2 Prod | Total | HHV
1.0001 |  | 7.3717 | 1.708 | 2.0687 | 0.56198 | 5.6746 | 0.0072527 | 8.3126 | 10317.4032
Flue Gas | Exc O2% | Act O2 | O2 | CO2 | H2O | N2 | SO2 | Total | LHV
Analysis | 3 | 1.7593 | 0.051241 | 2.0687 | 0.56198 | 5.8446 | 0.0072527 | 8.5337 | 9721.8721
|  | No. Moles | 0.0016013 | 0.047005 | 0.031195 | 0.20863 | 0.00011321 | 0.28855
|  | Mol Fract | 0.0055497 | 0.1629 | 0.10811 | 0.72305 | 0.00039234 | 29.5747 | Mol Wt.
Fuel Flow | Prod Flow | Fly ash % | With ash | Ash Load | Gas Temp | Heat Rel | ACFM |  | Comp
804049.8022 | 6861539.0553 | 80 | 6899683.1779 | 1.2302 | 800 | 8295706001.9649 | 3617535.4998 |  | 1.237

## Fuel Mix
COMBUSTION ANALYSIS
Site Location |  |  |  |  | Std. Amb. Temperature |  |  | 517.0316 | Deg R
Fuel Designation |  | 1 | 1E,2W | East | Std. Amb. Pressure |  |  | 14.4498 | Psia
Site Elevation |  |  | 468 | Ft | Std. Amb. Pressure |  |  | 29.4188 | Bar
Ambient Temperature |  |  | 60 | Deg F | Atmospheric Density |  |  | 0.075005 | Lbm/Cuft
%Fuel1 | 90 | %Fuel2 | 10
Ult Fract | Formula | Air/Fuel | Air | CO2 prod | H2O prod | N2 prod | SO2 prod |  | Htg Value
0.6933 | C | 11.51 | 7.9799 | 2.5403 | 0 | 6.1329 | 0 |  | 9770.6769
0.044553 | H2 | 34.29 | 1.5277 | 0 | 0.39817 | 1.1741 |  |  | 2721.9489
0.076045 | O2 | -4.3159 | -0.32821 | 0 | 0 | -0.25216 |  |  | 0
0.013189 | N2 | 0 | 0 | 0 | 0 | 0.013189 |  |  | 0
0.0064012 | S | 4.32 | 0.027653 | 0 | 0 | 0.021252 | 0.01279 |  | 25.4767
0.092297 | ASH | 0 | 0 | 0 | 0 | 0 |  |  | 0
0.074211 | H2O | 0 | 0 | 0 | 0.074211 | 0 | 0 |  | 0
Lbs Fuel |  | Air/Fuel | Stoich O2 | CO2 Prod | H2O Prod | N2 Prod | SO2 Prod | Total | HHV
1 |  | 9.207 | 2.1333 | 2.5403 | 0.47238 | 7.0893 | 0.01279 | 10.1147 | 12518.1025
Flue Gas | Exc O2% | Act O2 | O2 | CO2 | H2O | N2 | SO2 | Total | LHV
Analysis | 3 | 2.1973 | 0.063998 | 2.5403 | 0.47238 | 7.3015 | 0.01279 | 10.3909 | 12017.5228
|  | No. Moles | 0.002 | 0.05772 | 0.026221 | 0.26064 | 0.00019963 | 0.34678
|  | Mol Fract | 0.0057673 | 0.16644 | 0.075612 | 0.7516 | 0.00057568 | 29.9637 | Mol Wt.
Fuel Flow | Prod Flow | Fly ash % | With ash | Ash Load | Gas Temp | Heat Rel | ACFM |  | Comp
662696.7639 | 6886042.4243 | 80 | 6934974.5075 | 1.5931 | 800 | 8295706001.9649 | 3583317.8841 |  | 1.0195